SECTION 23 82 14 – CHILLED BEAMS

- GENERAL

      - SUMMARY

        - Section Includes:

          - Active chilled beam units specified herein per the lengths and quantities indicated on the Drawings and Schedules.

      - ACTION SUBMITTALS

        - Product Data: For each type of product.

        - Shop Drawings:

          - Plans, elevations, sections, mounting and attachment details.

          - Data Sheet:  Indicate materials of construction, finish, and mounting details; and performance data including throw and drop, static-pressure drop, and noise ratings.

          - Room Equipment Layout Schedule:  Indicate Drawing designation, room designation, full equipment layout detail within room including: quantity, model number, size, and accessories furnished.

          - Finishes – as needed.

        - Product Schedule: For active chilled beam units.

      - REFERENCE STANDARDS

        - AHRI Standard 410 – Standard for Forced-Circulation Air-Cooling and Air-Heating Coils

        - AHRI 1240-2017- Performance Rating of Active Chilled Beams.

        - ASHRAE Standard 55 – Thermal Environmental Conditions for Human Occupancy

        - ASHRAE Standard 62.1 – Ventilation for Acceptable Indoor Air Quality

        - ASHRAE Standard 70 – Method of Testing the Performance of Air Outlets and Air Inlets

        - ASHRAE Standard 90.1 – Energy Standard for Buildings Except Low-Rise Residential Buildings

        - ASHRAE Standard 90.2 – Energy-Efficient Design of Low-Rise Residential Buildings

        - ASHRAE 200-2018 - Methods of Testing Chilled Beams

        - ASTM Standard 653 - Standard Specification for Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot-Dip Process

        - ASTM Standard D610 – Standard Practice for Evaluating Degree of Rusting on Painted Steel Surfaces

        - ASTM Standard D714 – Standard Test Method for Evaluating Degree of Blistering of Paints

        - ASTM Standard D1308 – Standard Test Method for Effect of Household Chemicals on Clear and Pigmented Organic Finishes

        - ASTM Standard D1654 – Standard Test Method for Evaluation of Painted or Coated Specimens Subjected to Corrosive Environments

        - ASTM Standard D4752 – Standard Practice for Measuring MEK Resistance of Ethyl Silicate (Inorganic) Zinc-Rich Primers by Solvent Rub

        - NFPA 70- National Electric Code

        - ASTM C 534 / ASTM C 1427 - Standard Specification for Preformed Flexible Elastomeric Cellular Thermal Insulation in Sheet and Tubular Form

        - ASTM C 1534 - Standard Specification for Flexible Polymeric Foam Sheet Insulation Used as a Thermal and Sound Absorbing Liner for Duct Systems

        - ASTM D 1056, 2C1 - Standard Specification for cellular materials, both Sponge (Open Cell) and Expanded (Closed Cell)

        - ASTM E 84, UL723 - Standard Test Method for Surface Burning Characteristics of Building Materials

        - ASTM G21/C1338 - Standard Test Method for Determining Fungi Resistance of Insulation Materials and Facings

        - NFPA 90A - Standard for the Installation of Air-Conditioning and Ventilating Systems

        - NFPA 90B - NFPA 90A, 90B - Standard for the Installation of Air-Conditioning and Ventilating Systems

        - UL 181 - Standard for Safety Factory-Made Air Ducts and Air Connectors

        - UL 94 5VA - Classification and Flame-Retardant Thermoplastics

        - Division 23 – Heating, Ventilation and Air Conditioning (HVAC)

      - INFORMATIONAL SUBMITTALS

        - Mechanical Data:

          - Coil piping selection

          - Induction selection

          - Coil finish selection

          - Handing selection

          - Inlet size selection

          - Face grille selection

          - Paint color selection

          - Insulation requirements

          - Plenum finish and hanging bracket selection

        - Data Sheet Performance Information:

          - Cooling and heating performance

          - Primary air, induced air and supply air CFMs

          - Airside pressure drops

          - Water flow rates – Cooling and Heating

          - Waterside pressure drops

          - Supply air temperatures

          - Sound levels

        - IOM Data

          - Unit weights and dimensions

          - Ceiling assembly and mounting bracket details

          - Border detail for ceiling suspension integration

          - Manufacturers recommendations for installation

      - QUALITY ASSURANCE / CONTROL

        - Product Options: Drawings indicating size, profiles, and dimensional requirements of active beam units and are based on the specific system indicated.

        - Electrical Components, Devices and Accessories: Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

        - Active chilled beams and accessories shall be rated and tested for pressure as shown on the Drawings.

        - Identification: Label each Induction Unit with the appropriate tagging identifier.

      - WARRANTY

        - Manufacturer shall provide a parts-only warranty for a period of twelve (12) months from the initial startup-up, or eighteen (18) months from date of shipment, whichever occurs first.

        - Labor warranty shall be the responsibility of the Installing Contractor(s)

        - Products will be free from defects in material and manufacture. Installing contractor shall document products were installed in accordance with: 1) Manufacturer’s installation guidelines, 2) Recommended Start-Up procedures, and 3) Recommended maintenance procedures.

        - Provide documented records indicating that Manufacturer’s normal conditions for service have been maintained during stated warranty period.

- PRODUCTS

      - PERFORMANCE REQUIREMENTS

        - Capacities and Characteristics:

          - See Schedule and Notes on Plans

      - MANUFACTURERS

        - Basis of Design: Carson Solutions Model CB-H24.

        - Alternate Manufacturers: In order to attain prior approval as an alternate manufacturer, the manufacturer shall provide ALL following documents for consideration:

- Prior approval documentation from [Owner] [School District] and shall provide documentation of successful execution and operation for three (3) years for no less than five (5) separate projects.

- A detailed CAD drawing, Factory Performance Data must be submitted to the Engineer to be considered for Prior Approval. The manufacturer must also include a detailed Table of Conformance detailing acceptance or rejection of all specification sections.

        - If Basis of Design Manufacturer is not provided, Contractor shall be responsible and bear all financial risks for all costs associated with the substitution of an alternative product including, but not limited to additional field labor, structural changes, and attenuation to meet project acoustical requirements. All consequential damages, project delays, and additional Engineering costs shall be borne by the Mechanical Contractor.

      - CONSTRUCTION

        - Furnish and install CARSON SOLUTIONS CB-H24 series dual slot active chilled beams of sizes and capacities as indicated on the drawings and within the mechanical equipment schedules. The quantity and length of the beams shall be as shown in the drawings.  The beams shall be constructed and delivered to the job site as single units.

        - Casing to be manufactured from 20 GA G-60 galvanized sheet steel and 20 GA CRS sheet steel conforming to ASTM-653 standards. Casing shall house an integral hydronic coil and a primary air plenum delivering air to a series of induction nozzles. A single round primary air connection shall be mounted on either side or top of the unit as indicated in the Drawings. All sheet metal joints in the primary air plenum and air connection spigot shall be sealed airtight.

  - (OPTIONAL PAINT): Units with exposed border shall have the plenum painted to match the front face color selection.

        - The face of the beam shall consist of a room air induction section of 51% free area perforated steel flanked by two linear supply slots. The entire visible face section shall be finished in WHITE powdercoated paint or as specified by the architect.  Maximum overall height shall not exceed nine (8.5) inches for inlet sizes 4”, 5”, and 6”.

          - If a non-standard 8” supply inlet is selected whereas the plenum height will be a maximum of 11 inches.

        - Face panel shall be fully hinged to allow access to hydronic coil. The hinge face panel to be also reversable to allow the swing direction to be changed if necessary by the installing contractor.

        - Beams shall be provided with side and end details which will allow its integration into the applicable (nominal 24 inch wide) acoustical ceiling grid as specified by the architect.

  - (OPTION): Tegular Border Style Casing

- The manufacturer will provide an edge detail to allow the beam to sit flush with the face of the T-bar ceiling.

- Tegular profiles of 9/16” and 15/16” shall be accommodated.

- Exposed Mounted Border Style Casing shall include factory mounted Coanda plates to ensure horizontal discharge of the supply air with a nominal width of 36 inches.

        - K-Factor Label and Air Pressure Commissioning Port: Beams shall be fitted with an uncapped air pressure tap for measuring the static pressure differential between the primary air plenum and the room. Air pressure port shall be accessible from the hinged face panel.  Each active chilled beam shall be provided with an airflow calibration label affixed showing primary airflow rate for given nozzle configuration at varying plenum pressures.

        - Hydronic Coil:  Active Chilled Beams shall be provided with an integral hydronic coil providing cooling and heating performance as indicated on plans and schedules. The coils shall be mounted horizontally and shall be manufactured per the following details:

          - Coils shall have a continuous aluminum plate fin surface, with seamless copper tubes mechanically expanded into aluminum fin collars for secure, crack-free bonding.

          - Copper tube connections shall be ½” O.D. x 0.028” thick.

          - Aluminum fins shall have a minimum fin thickness of 0.0055”. [0.0075”/0.0095”] optional.

          - Aluminum fin spacing shall not exceed 8 fins per inch.

          - Coils shall be tested to a minimum of 360 psi and a max of 500 psi. air pressure under water.

          - Coil normal operating pressure is rated at 250 psig max up to 300°F. The maximum working pressure should not exceed 360 psi.

          - (OPTION): Manual air vents shall be located at each coil circuit high point.

          - Water drains shall be located at each coil circuit low point.

          - Coils shall be circuited for [2 or 4 pipe] operation.

          - Coil connections shall be ½” plain copper pipe or ½” NPT male threaded fittings.

          - Coils shall be delivered cleaned and flushed.

          - Coils to be AHRI 410 certified by coil manufacturer.

        - (OPTIONAL COIL FITTINGS): The chilled water coil shall be provided with ½” NPT male threaded fittings where specified. These fittings must be suitable for field connection to a similar (½” NPT) female flexible hose spigot and shall be at least 1½” long to facilitate field connection (by others).  Other fitting sizes and connections are available from factory.

        - [OPTION] Stainless Steel Braided Hoses Kit Assemblies

            - One end connection shall swivel to allow for equipment movement during operation.

            - ½” – 1” shall be made of CPE (Chlorinated Polyethylene).

            - 1¼” – 2” shall be made of EPDM (Ethylene Propylene Diene Monomer).

            - Maximum working pressures:

            - 500# WPSI Static (½” – 1”)

            - 200# WPSI Static (1¼” – 2”)

            - Maximum temperature rating: 212°F

        - [OPTION] Provide 1/8” or ½” thick thermal insulation applied to the exterior of the primary air plenum to prevent condensation forming on the outside of the unit casing and the interior surfaces of the primary air chamber. Technical data sheet to be provided by request.

        - Source Quality Control: Comply with ASHRAE 200, AHRI-410, and AHRI 1240

          - Coil capacity rated in accordance with AHRI 410-2000, Forced Circulation Air-Cooling & Air-Heating Coils

          - Capacity performance and sound levels of induction coils (chilled beams) rated in accordance with ASHRAE 200-2018, Methods of Testing Chilled Beams

          - Capacity and performance of active chilled beams coils shall be rated in accordance with AHRI 1240-2017, Performance Rating of Active Chilled Beams.

      - GENERAL PROTECTION REQUIREMENTS

        - Protect finishes on exposed surfaces from damage by applying a removable, temporary protective covering at the factory before shipping.

        - Protect coil and piping openings with removable end caps before shipping.

        - Protect duct connection openings with removable end caps before shipping.

- EXECUTION

      - EXAMINATION

        - Examine areas to receive displacement inductions units for compliance with requirements for installation tolerances and other conditions affecting performance of the Work.

        - Examine roughing-in for duct, piping and wiring to verify actual locations of connections before installation.

        - Proceed with installation only after unsatisfactory conditions have been field corrected.

        - Ensure all units received have appropriate and individual tagging identifiers.

          - Chilled Beam manufacturer must label each shipping package AND equipment, including accessories, with room by room tags, along with model numbers for ease of site coordination.

      - INSTALLATION

        - Coordinate the size, tagging and capacity of the beams to their proper location.

        - Install active chilled beam level and plumb in accordance with manufacturer’s IOM documentation.

        - Chilled beams up to five feet in length shall be independently suspended from the structure above by four (4) threaded rods of ⅜” diameter. For beams beyond six feet in length, six (6) threaded rods of ⅜” diameter shall be used. Wire rope is allowable as a substitute.

        - Install piping adjacent to beams to allow service and maintenance.

        - Installing overhead beams according to Division 23 – Heating, Ventilation and Air Conditioning (HVAC) Section 23 05 29 “Hangers and Supports for HVAC Piping and Equipment”.

      - PIPING CONNECTIONS

        - Comply with requirements for piping specified in Section 232113 "Hydronic Piping" and Section 232116 "Hydronic Piping Specialties." Drawings indicate general arrangement of piping, fittings, and specialties.

        - Comply with requirements for general duty valves specified in Section 230523.11 "Globe Valves for HVAC Piping," Section 230523.12 "Ball Valves for HVAC Piping," and Section 230523.15 "Gate Valves for HVAC Piping."

        - Make piping connections to chilled beam units at locations indicated on Drawings.

        - Verify any and all identification tags are visible.

        - Verify control connections are complete to control valves as needed.

        - Verify controls respond to inputs specified.

      - DUCT CONNECTIONS

        - Comply with requirements for ductwork specified in Section 233113 "Metal Ducts." and Section 233346 "Flexible Ducts." Drawings indicate general arrangement of ductwork.

        - Make ductwork connections to chilled beam units at locations indicated on Drawings.

        - Where installing ductwork adjacent to chilled beams, allow space for service and maintenance.

      - ELECTRICAL CONNECTIONS

        - Connect wiring in accordance with Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

        - Ground equipment in accordance with Section 260526 "Grounding and Bonding for Electrical Systems."

      - CONTROLS

        - Comply with requirements for controls specified in Section 230923 "Direct Digital Control (DDC) System for HVAC and Section 230993.11 "Sequence of Operations for HVAC DDC."

      - IDENTIFICATION

        - Identify hydronic piping and valves. Comply with requirements specified in Section 230553 "Identification for HVAC Piping and Equipment."

      - CLEANING AND PROTECTION

        - Protect exposed surfaces of displacement induction units from damage with factory-installed protective covering. Maintain covering in place until start of unit testing and balancing.

        - Protect chilled beam units’ water connections with factory-installed protective covers and keep them covered until making final field piping connections.

        - Clean chilled beam units inside and out to a factory-new condition.

        - Reject damaged chilled beam units and replace them with new units.

        - Only if acceptable to the Owner, minor damage to finishes may be repaired as required to restore the beams to factory-new appearance. Any variation in visual appearance between factory and repaired finish shall be rejected.

      - FIELD QUALITY CONTROL

        - Testing Agency: [Owner] [Engineer] [Contractor] shall engage a qualified testing agency to perform tests and inspections.

        - Perform tests and inspections with the assistance of a factory authorized service representative.

        - Tests and Inspections:

          - Leak Test: After installation, fill the system with water under design pressure and test for leaks. Repair leaks and retest until no leaks exist.

        - Chilled beam units will be considered defective if they do not pass tests and inspections.

        - Prepare test and inspection reports, and route to Owner, Architect, Engineer, and Contractor.

      - ADJUSTING

        - Occupancy Adjustments: When requested, within [12] months from date of Substantial Completion provide on-site assistance in adjusting system to suit actual occupied conditions.

      - DEMONSTRATION

        - Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain displacement induction ventilation units.

END OF SECTION 238214