SECTION 238214 - DISPLACEMENT INDUCTION VENTILATION ACTIVE CHILLED BEAMS

      - SUMMARY

        - Section Includes:

          - Floor mounted, cabinet style, displacement induction ventilation active chilled beams and associated cabinet accessories as detailed on Plans and Schedule.

      - ACTION SUBMITTALS

        - Product Data: For each type of product.

        - Shop Drawings:

          - Plans, elevations, sections, mounting and attachment details.

          - Data Sheet:  Indicate materials of construction, finish, and mounting details; and performance data including throw and drop, static pressure drop, and noise ratings.

          - Room Equipment Layout Schedule:  Indicate drawing designation, room designation, full equipment layout detail within room to include: quantity, model number, size, and accessories furnished.

          - Cabinet Finishes – as specified

        - Product Schedule: For displacement induction vertical (DIV)chilled beams

      - INDUSTRY REFERENCE STANDARDS

        - AHRI Standard 410-2023 - Standard for Forced-Circulation Air-Cooling and Air-Heating Coils

        - AHRI 1240-2017 - Performance Rating of Active Chilled Beams

        - ANSI Standard 1260-2010 - Acoustical Guidelines for Schools

        - ASHRAE Standard 55-2017 - Thermal Environmental Conditions for Human Occupancy

        - ASHRAE Standard 62.1-2022 - Ventilation for Acceptable Indoor Air Quality

        - ASHRAE Standard 70-2006 - Method of Testing the Performance of Air Outlets and Air Inlets

        - ASHRAE Standard 90.1-2022 - Energy Standard for Buildings Except Low-Rise Residential Buildings

        - ASHRAE Standard 90.2-2018 - Energy-Efficient Design of Low-Rise Residential Buildings

        - ASHRAE 200-2024 - Methods of Testing Chilled Beams

        - ASTM Standard A653/A653M-22 - Standard Specification for Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot-Dip Process

        - ASTM Standard D610-08 (2019) - Standard Practice for Evaluating Degree of Rusting on Painted Steel Surfaces

        - ASTM Standard D714-02 - Standard Test Method for Evaluating Degree of Blistering of Paints

        - ASTM Standard D1308-20 - Standard Test Method for Effect of Household Chemicals on Clear and Pigmented Organic Finishes

        - ASTM Standard D1654-08 - Standard Test Method for Evaluation of Painted or Coated Specimens Subjected to Corrosive Environments

        - ASTM Standard D4752-20 - Standard Practice for Measuring MEK Resistance of Ethyl Silicate (Inorganic) Zinc-Rich Primers by Solvent Rub

        - NFPA 70 - National Electric Code

        - ASTM C 534 / ASTM C 1427 - Standard Specification for Preformed Flexible Elastomeric Cellular Thermal Insulation in Sheet and Tubular Form

        - ASTM C 1534 - Standard Specification for Flexible Polymeric Foam Sheet Insulation Used as a Thermal and Sound Absorbing Liner for Duct Systems

        - ASTM E84-21 (UL723) - Standard Test Method for Surface Burning Characteristics of Building Materials

        - NFPA 90A-2024 - Standard for the Installation of Air-Conditioning and Ventilating Systems

        - NFPA 90B-2024 - Standard for the Installation of Warm Air Heating and Air-Conditioning Systems

        - UL 181 - Standard for Safety Factory Made Air Ducts and Air Connectors

        - UL 94-5VA - Test for Flammability of Plastic Materials for Parts in Devices and Appliances Classification and Flame-Retardant Thermoplastics

      - INFORMATIONAL SUBMITTALS

        - Product Data:  For each product indicated, include the following:

          - Data Sheet:  Indicate materials of construction, finish, mounting details, and performance data including throw and drop, static pressure drop, and sound ratings per octave band.

          - Room Equipment Layout Schedule:  Indicate Drawing designation, room designation, full equipment layout detail within room to include quantity, model number, size, and accessories furnished.

        - Coordination Drawings: Floor plans, reflected ceiling plans, sections, and BIM model, drawn to scale, showing the items described in this Section and coordinated with all building trades.

      - QUALITY ASSURANCE / CONTROL

        - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction and marked for intended use.

        - Identification: Label each induction displacement induction unit with the appropriate tagging identifier.

      - WARRANTY

        - Manufacturer shall provide a parts-only warranty for a period of twelve (12) months from the initial startup-up, or eighteen (18) months from date of shipment, whichever occurs first.

        - Labor warranty shall be the responsibility of the Installing Contractor(s)

        - Products will be free from defects in material and manufacture. Installing contractor shall document products were installed in accordance with: 1) Manufacturer’s installation guidelines, 2) Recommended Start-Up procedures, and 3) Recommended maintenance procedures.

        - Provide documented records indicating that Manufacturer’s normal conditions for service have been maintained during stated warranty period.

- PRODUCTS

      - PERFORMANCE REQUIREMENTS

        - Capacities and Characteristics:

          - See Schedule and Notes on Plans

      - MANUFACTURERS (PICK PROJECT BIDDING SCENARIO (A, B, C)

        - Basis of Design: Carson Solutions Model QLCI-No Substitute

        - Basis of Design: Carson Solutions Model QLCI w Voluntary Alternates

        - Basis of Award: Basis of Award for the Mechanical Contract shall be based on Basis of Design. Acceptance of any Alternates shall not relieve the Manufacturer from adhering to the Product Specifications.

        - Alternate Manufacturers must provide the Mechanical Engineer with a detailed description of the proposed equipment ten (10) days prior to Bid. Include all exceptions and clarifications to the Specification in the document.

        - Drawings: A detailed CAD drawing of induction displacement ventilation units       and specified accessories

        - Factory Performance Data:  Provide pre-submittal Data for all models listed on the Schedule to include compliance with ANSI Standard S12.60, Acoustical Performance Criteria, Design Requirements, and Guidelines for Schools.

        - Compliance Data Sheet: Include a detailed Chilled Beam Compliance Form detailing compliance or deviation from the listed specification sections (see Table in Division 23 Specification).

        - Third Party Testing: Submit documentation of independent, third-party testing of equipment performance to Engineer. Use of SF6 tracer gas in laboratory shall provide for clear measurement of contaminants. Testing shall be certified for the following tests:

- Ventilation Effectiveness: Validate CFD modeling of Ventilation Effectiveness in both heating and cooling mode proving stratified conditions in all modes of cooling and heating.

- Thermal Comfort: Provide laboratory verified values and CFD modeling proving Thermal Comfort adherence to ASHRAE 55 limit of 5.4°F “from toes to nose.”

- Sound Levels: Provide data that indicates compliance with ANSI Standard 1260-2010, Acoustical Guidelines for Schools. Units must meet 35 dBA or less.

        - Basis of Design: Carson Solutions Model QLCI, Acceptable Alternates: Dadanco Model Displacement IDU, Price Model ACBC

            - Manufacturer shall meet and exceed the Specification and Schedule items

- General Note: If Basis of Design Manufacturer is not provided, the Mechanical Contractor shall be responsible and bear all financial risks for all costs associated with the substitution of an alternative product including, but not limited to additional field labor, structural changes, architectural considerations, and sound attenuation. All consequential damages, project delays, and additional Engineering costs shall be borne by the Mechanical Contractor.

      - CONSTRUCTION

        - Basic Unit Description:

          - Assembly shall consist of a displacement induction ventilating air-conditioning terminal housed in an architecturally approved enclosure. All internal sheet metal components shall be galvanized to inhibit corrosion. If perforated panels are utilized in the construction internal components shall be painted black to reduce visibility.

          - Terminal shall consist of round duct connection(s), a series of metal injection nozzles, integral two (2) or four (4) pipe heat transfer coil, and an integral perforated equalizing grid behind the discharge louver to reduce velocity and noise.

          - Primary air and water piping connections shall be configured to allow connection of up to three units in series.

          - No integral fans, compressors, or other components requiring a power supply shall be allowed within the terminal room equipment.

          - Displacement terminals must be able to handle 100% outside air temperatures between 50°F to 55°F and provide supply air to the space so that the temperature gradient through the occupied space falls within the guidelines of ASHRAE Standard 55, Thermal Environmental Conditions for Human Occupancy.

          - Displacement terminal units shall have a 3” high toe kick-plate to elevate the painted cabinet above the floor level.  Maximum cabinet height to the top of the unit above the floor level shall not exceed thirty (30) inches.

          - The heat transfer coil shall be easily removable from the cabinet and fully accessible from the front panel for ease of cleaning.

            - Coils shall have a continuous aluminum plate fin surface, with seamless copper tubes mechanically expanded into aluminum fin collars for secure, crack-free bonding.

            - Copper tube connections shall be ½” O.D. x 0.028” thick.

            - Aluminum fins shall have a minimum fin thickness of 0.0010.

            - Aluminum fin spacing shall not exceed 8 fins per inch.

            - Coils shall be tested to a minimum of 300 psi working pressure and a max of 450 psi air pressure under water.

            - Coil normal operating pressure is rated at 250 psi max up to 200°F. The maximum working pressure should not exceed 300 psi.

            - Manual air vents shall be located at each circuit high point.

            - Coils shall be circuited for two (2) or four (4) pipe operation.

            - Coils shall have integral drain fittings on each circuit low point.

            - Coil connections shall be ½” NPT male threaded fittings.

            - Coils shall be delivered cleaned and flushed.

          - Condensate drain pans shall be constructed of CRS steel or Stainless Steel.  Condensate drain pans must be easily accessible for cleaning via the removable front panel.

            - A ½” OD plastic drain fitting is terminated at roughly 2” below the condensate drain pan.

            - Provide an atrium style drain fitting to prevent clogging.

            - Condensate drain fittings shall be factory capped and must be removed if Piping Contractor is field installing condensate piping.

        - Cabinet Construction Details:

          - Cabinets shall be constructed of minimum 16-gauge A1008 CS Type B cold rolled sheet steel and finished with powder coat paint in a standard or custom color as selected by Architect. (see Notes on Schedule). Architect must approve the custom color.

          - Finish shall be DuroCoat Sand Matte Textured Powder Coating to hide small scratches and fingerprints. Smooth, non-textured gloss paint finishes are NOT acceptable due to high-traffic fingerprint pickup, and highly reflective properties.

          - [Provide 0.75” thick custom laminate counter tops in wood grain or solid colors. Architect shall select from Manufacturer’s Color Selection Chart.]

          - Construction shall be sufficient to allow a 250 lb maintenance personnel to stand on the cabinet without any deflection.

          - Cabinet structure must have a front panel center installed mullion, bisecting each diffuser face panels into two equal sections, thereby providing each cabinet unit with a minimum of four (4) separate sections (two (2) supply outlet panels and two (2) return air panels) for rigidity and ease of removal. Diffusers with single face access panels will NOT be acceptable due to extreme removal and reduced rigidity concerns.

          - Face panels shall be louvered, pencil-proof, and at least a 45 percent free area.  Cabinet structure must have an integral front center panel mullion for structural rigidity. If perforated panels are provided all internal components such as coils, condensate drain pans, and sheet metal block-offs must be painted satin black to minimize mechanical equipment display.

          - Front louvers must be easy to remove and be less than 42” length for rigidity and ease of access.

            - Front induction panels shall be lockable with multiple cam locks to allow for easy access to the hydronic coil. Sheet metal, bolts, or TEK screws are NOT an acceptable means for securing induction panel assembly or removal for routine maintenance.

            - The top surface of cabinet shall be flat and allow the entire surface to be used as a bookshelf or other useable storage.

            - The cabinet shall have structural frame around louver opening to ensure structural strength when louver is removed for service.

            - Cabinet shall be rated to support a 250 lb load without deflection.

          - Supply Air Diffuser Plate: An angled perforated steel plate shall be mounted on the supply air discharge to promote even air distribution into the occupied space.

        - Duct and Pipe Chase and Additional Enclosures

          - Furnish an architecturally approved solid cover with a matte finish that matches the cabinet color and construction for all required units to conceal all vertical ductwork and piping to the units.  See Plans for locations. Field measure height requirements before release of order.

        - Displacement Induction Operation Description:

          - Outside air at the primary airflow rate listed on the Plans and Schedules shall be conditioned and delivered displacement units at the scheduled supply air conditions.

            - This conditioned primary air shall be ducted to the lead connection(s) of a series of displacement induction terminals.

            - Injection of the primary air through metal induction nozzles shall induce room air through an integral heat transfer coil and recondition return airstream prior to mixing with primary air.

            - The mixture of 2/3 induced room air and 1/3 primary air shall pass through an equalization plate and discharge to the occupied space at the scheduled outlet velocities to assure displacement ventilation during system operation. Primary outside air that exits the top of the cabinet is not acceptable as the mixed air is not introduced into the breathing zone per ASHRAE 62.1-2022.  Twenty percent excess outside air must be provided in heating mode for units that use primary air to drive vertical airflow into the occupied space breathing zone.

            - Performance Requirements:

              - Diffuser Exit Air Velocity: Measured at five (5) feet from the diffuser

              - Primary Air Plenum Pressures: Less than or equal to scheduled pressures.

              - Room Sound Levels:  Less than or equal to scheduled dBA and NC levels

              - Sensible Cooling and Heating Loads: Equal to or greater than scheduled levels

              - Primary Air, Induction Rates, or Supply Air CFMs

            - [Rear Fin Tube Convective Heating Elements: Provide 2 row fin tube elements that extend the length of the induction displacement unit.  The outlet louver top panel shall be pencil-proof and integral to the cabinet.  Outlet louver top panel shall allow for removable access for cleaning and provided with cam locks. Sheet metal screws, bolts, or TEK screws are NOT an acceptable means for removable panels].

        - K-Factor Label and Air Pressure Commissioning Port: All displacement induction diffusers shall be fitted with an uncapped air pressure tap for measuring the static pressure differential between the primary air plenum and the room. Air pressure ports shall be accessible behind the upper-left return/induction front face panel.  Each displacement unit shall be provided with an affixed airflow calibration label indicating primary airflow rate for each nozzle configuration at varying plenum pressures.

        - Description for Acoustic Performance (Conformance to ANSI S12.60)

          - Terminals shall be sized and selected such that their collective noise generation shall not contribute to a classroom noise level exceeding an A-Weighted value of 35 dBA per ANSI Standard S12.60-2010 Acoustical Guidelines for Schools.  Noise Criteria (NC) sound levels of the individual terminals shall not exceed NC-27.

        - [Accessories and Options:]

          - [Architectural Cabinet Sections]: All architectural cabinet sections shall be constructed of the same gauge metal and paint finish as specified for main unit cabinet

            - Basic Utility Compartment: Sections with removable access door and knotched piping passage as detailed on Plans.

            - Basic Bookshelf Selection: Sections with custom adjustable shelving, and knotched piping passage as detailed on Plans.

            - Blank Filler Section: Include horizontal fill section that can be cut to length, floor angles, wall offset strips, and mounting hardware as detailed on Plans

            - Vertical Duct Cover: For entrance of overhead primary air. Includes wall angles, optional removable access doors/covers, cover plates, and countersunk screws as detailed on Plans.

          - [Stainless Steel Braided Flexible Hose Kit Assembly]

            - Provide [Swivel FNPT] [Swivel Union] [Fixed Tailpiece] as required

            - End connections shall swivel to allow for equipment movement during operation.

            - Maximum working temperature / pressures: 300# psi /212 deg F

            - Provide stainless steel ferrules on each end of the hose.

          - [Architectural Laminate Countertops]

            - Provide custom durable 0.75” thick laminate counter tops in wood grain or solid colors. General Contractor shall field measure and install laminate countertops only after the Displacement Induction Vertical chilled beams and accessories are installed. Architect shall select from Manufacturer’s Color Selection Chart.

          - [Bipolar Ionization]

            - Factory mounted Bi-Polar Ion (BPI) generator shall be supplied by chilled beam Manufacturer, field mounted by Mechanical Contractor, and field wired by Electrical Contractor. The generator shall be mounted within the primary air plenum of the cabinet such that ions immediately attack room air during the induction process.

            - Exterior mounting by others is not allowed, and the units must be easily accessible following removal of the front air panel.

            - Negatively and positively charged ions shall be generated by Dielectric Barrier Discharge

            - The Manufacturer of the ion generator shall provide documentation indicating compliance with UL 867 and UL 2998 for ozone levels.

            - Ion generation shall be calibrated to provide ion readings between 350 to 1,500 ions/cm3.

            - An airflow proving switch shall be provided to disable the ion generator during unoccupied modes.

            - Electrical power shall be supplied to the ion generator by Division 26, 24 volts, 2-wire. One (1) power source shall be required per room for the ion generator.

        - Source Quality Control: Comply with ASHRAE 200, AHRI-410, ANSI 1260, and AHRI 1240

          - Capacity performance and sound levels of induction coils (chilled beams) shall be rated in accordance with ASHRAE 200-2018, Methods of Testing Chilled Beams

          - Coil capacity rated in accordance with AHRI 410-2000, Forced Circulation Air-Cooling & Air-Heating Coils

          - Sound levels shall be certified in accordance with ANSI Standard 1260, Acoustics for Classrooms

          - Capacity and performance of active chilled beams coils shall be rated in accordance with AHRI 1240-2017, Performance Rating of Active Chilled Beams.

      - GENERAL PROTECTION REQUIREMENTS

        - Protect finishes on exposed surfaces from damage by applying a removable, temporary protective covering at the factory before shipping.

        - Protect coil and piping openings with removable end caps before shipping.

        - Protect duct connection openings with removable end caps before shipping.

- EXECUTION

      - EXAMINATION

        - Examine areas to receive displacement induction ventilation chilled beams for compliance with requirements for installation tolerances and other conditions affecting performance of the Work.

        - Examine roughing-in for duct, piping, and wiring to verify actual locations of connections before installation.

        - Proceed with installation of the chilled beams, and accessories only after unsatisfactory conditions have been corrected to include, but not limited to confirming that the floor is level,  and that adjacent walls are plumb. Proceed with installation only when the adverse conditions have been field corrected.

        - Ensure all units received must have appropriate and individual tagging identifiers.

          - Manufacturer must label each shipping package and equipment, including accessories, with room tags, and Model numbers for ease of site coordination.

        - Installation and operation of the units shall be in strict accordance with the latest issue of the Manufacturer’s Installation, Operation, and Maintenance (IOM) Manual

      - INSTALLATION

        - Displacement induction units and accessories shall arrive on site as a factory assembled, housed cabinet structure.  Cabinets sections shall only require secure attachment to the wall and associated air and water connections.  Field erection of cabinet framing support members or diffuser cabinet housing panels shall be not allowed due to excessive field labor requirements and uniform fit and finish variability.

        - Install displacement induction level and plumb in accordance with manufacturer’s Installation, Operation, Maintenance (IOM) Manuals.

        - Arranged installation of units to provide access space for proper service and maintenance.

      - PIPING CONNECTIONS

        - Comply with requirements for piping specified in Section 232113, “Hydronic Piping" and Section 232116 "Hydronic Piping Specialties." Drawings indicate general arrangement of piping, fittings, and specialties.

        - Comply with requirements for general duty valves specified in Section 230523.11 "Globe Valves for HVAC Piping," Section 230523.12 "Ball Valves for HVAC Piping," and Section 230523.15 "Gate Valves for HVAC Piping."

        - Make piping connections to displacement induction units at locations indicated on Drawings.

        - Where installing piping adjacent to displacement induction units, allow adequate space for service and maintenance.

      - DUCT CONNECTIONS

        - Comply with requirements for ductwork specified in Section 233113 "Metal Ducts." and Section 233346 "Flexible Ducts." Drawings indicate general arrangement of ductwork.

        - Make ductwork connections to displacement induction units at locations indicated on Drawings.

        - Where installing ductwork adjacent to displacement induction unit allow space for service and maintenance.

      - ELECTRICAL CONNECTIONS

        - Connect wiring in accordance with Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

        - Ground equipment in accordance with Section 260526 "Grounding and Bonding for Electrical Systems."

      - AUTOMATIC CONTROLS

        - Comply with requirements for controls specified in Section 230923 "Direct Digital Control (DDC) System for HVAC and Section 230993.11 "Sequence of Operations for HVAC DDC.

      - IDENTIFICATION

        - Identify hydronic piping and valves. Comply with requirements specified in Section 230553 "Identification for HVAC Piping and Equipment."

      - CLEANING AND PROTECTION

        - Protect exposed surfaces of displacement induction units from damage with factory installed protective covering. Maintain covering in place until start of unit testing and balancing.

        - Protect displacement induction units’ air connections with factory installed protective covers and keep them covered until making final field duct connections.

        - Clean displacement induction units inside and out to a factory new condition.

        - Reject damaged displacement induction units and replace them with new units.

        - Only if acceptable to the Owner, minor damage to finishes may be repaired as required to restore displacement induction units to factory-new appearance. Any variation in visual appearance between factory and repaired finish shall be rejected.

      - FIELD QUALITY CONTROL

        - Testing Agency: [Owner] [Engineer] shall engage a qualified testing agency to perform tests and inspections.

        - Perform tests and inspections with the assistance of a factory authorized service representative.

        - Tests and Inspections:

          - Leak Test: After installation, fill the system with water under design pressure and test for leaks. Repair leaks and retest until no leaks exist.

        - Displacement induction units will be considered defective if they do not pass tests and inspections.

        - Prepare test and inspection reports, and route to Owner, Architect, Engineer, and Contractor.

      - ADJUSTING

        - Occupancy Adjustments: When requested, within twelve (12) months from date of Substantial Completion provide on-site assistance in adjusting system to suit actual occupied conditions.

      - DEMONSTRATION

        - Engage a factory authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain displacement induction ventilation units.

END OF SECTION 238214

TABLE OF COMPLIANCE FORM – ALTERNATE MANUFACTURERS SHALL SUBMIT TO THE MECHANICAL ENGINEER TEN (10) DAYS BEFORE BID DATE

| SPECIFICATION SECTION | DESCRIPTION | COMPLIANCE (YES or NO) | REMARKS |
| --- | --- | --- | --- |
| 23 82 14.1.3 | Industry Reference Standards |  |  |
| 23 82 14.2.2.B.2.d.i | 3rd Party Testing - Vent Effectiveness |  |  |
| 23 82 14.2.2.B.2.d.ii | 3rd Party Testing – Thermal Comfort |  |  |
| 23 82 14.2.2.B.2.d.iii | Sound Level Testing per ANSI 1260 |  |  |
| 23 82 14.2.3.A.3 | Sloped Condensate Drain Pan with Drain |  |  |
| 23 82 14.2.3.A.7 | Cooling / Heating Coil |  |  |
| 23 82 14.2.3.B.1 | 16 Gauge Louvered Front Panels |  |  |
| 23 82 14.2.3.B.2 | Sand Matte powder coat paint |  |  |
| 23 82 14.2.3.B.3 | [¾” thick laminate countertops] |  |  |
| 23 82 14.2.3.B.5 | Four (4) separate S & R panels |  |  |
| 23 82 14.2.3.B.5 | Panels are less than 42” wide |  |  |
| 23 82 14.2.3.B.7 | Multiple Cam-Lock fasteners |  |  |
| 23 82 14.2.3.B.8 | Supply Air Diffuser |  |  |
| 23 82 14.2.3.D.1.d | Performance Requirements |  |  |
| 23 82 14.2.3.D.1.d | 2 row Finned Tube Heating |  |  |
| 23 82 14. 2.3.G.1.a | 16 gauge Utility Compartments |  |  |
| 23 82 14. 2.3.G.1.b | 16 gauge Basic Bookshelves |  |  |
| 23 82 14. 2.3.G.1.c | 16 gauge Filler Sections |  |  |
| 23 82 14. 2.3.G.1.c | 16 gauge Vertical Duct Cover |  |  |
| 23 82 14. 2.3.G.1.c | Stainless Steel Braided Hose Kits |  |  |
| 23 82 14.2.3.G.4 | Bipolar Ionization |  |  |